## F - Transmission Changes
New or Upgraded Transmission Facilities in EIPC 2023 Roll-Up Case
Includes ALL new/upgraded facilities (230 kV and above) that are projected to be in-service by 2019
PA | State(s) | From Bus # | From Bus Name | To Bus # | To Bus Name | Ckt | Voltage (kV) | Line Length (miles) | Expected In-Service Year | Planning Status | Project Type | Project Description
PJM | WV | 235378 | 01NMARTN |  |  |  | 138 | - | 2015-06-01 | Planned | Reliability | Add 44 MVAR Cap at New Martinsville
PJM | IL | 270678 | BYRON ; B |  |  |  | 345 | - | 2017-06-01 | Planned | Reliability | Remove Byron SPS upon completion of Byron - Wayne 345 kV
PJM | PA | 253975 | 15BI |  |  |  | 345 | - | 2016-06-01 | Planned | Reliability | 200 MVAR shunt reactor at Brunot Island 345 kV
PJM | PA | 253975 | 15BI |  |  |  | 345 | - | 2016-06-01 | Planned | Reliability | 200 MVAR shunt reactor on future Brunot Island – Carson 345 kV circuit
PJM | PA | 213579 | EDDYSTN |  |  |  | 345 | - | 2017-06-01 | Planned | Reliability | Install a second Eddystone 230/138 kV transformer
PJM | NJ | 228401 | MCKLTON |  |  |  | 230 | - | 2015-05-31 | Planned | Reliability | 50 MVAR shunt reactor at Mickleton 230 kV and relocate Mickleton #1 230 69 kV transformer
PJM | NJ | 227955 | CEDAR |  |  |  | 230 | - | 2016-06-01 | Planned | Reliability | +150/-100 MVAR SVC at Cedar 230 kV
PJM | IN | 243217 | 05DEQUIN |  |  |  | 345 | - | 2016-12-01 | Planned | Reliability | Install a 300 MVAR reactor at Dequine 345 kV
PJM | WV | 242508 | 05AMOS |  |  |  | 765 | - | 2016-06-01 | Planned | Reliability | Replace existing 150 MVAR reactor at Amos 765 kV substation on Amos – N. Proctorville - Hanging Rock with 300 MVAR reactor
PJM | IN | 243206 | 05DUMONT |  |  |  | 765 | - | 2016-12-31 | Planned | Reliability | Install 765 kV reactor breaker at Dumont 765 kV substation on the Dumont - Wilton Center line
PJM | OH | 242928 | 05MARYSV |  |  |  | 765 | - | 2015-06-01 | Planned | Reliability | Install 765 kV reactor breaker at Marysville 765 kV substation on the Marysville - Maliszewski line
PJM | KY | 242510 | 05BAKER |  |  |  | 765/345 | - | 2016-06-01 | Planned | Reliability | Change transformer tap settings for the Baker 765/345 kV transformer
PJM | NJ | 206255 | 28W WHRTN |  |  |  | 230 | - | 2015-06-01 | Planned | Reliability | Install -260/+40 MVAR SVC at West Wharton 230 kV substation
PJM | MD | 235488 | 01MONOCY |  |  |  | 230 | - | 2015-06-01 | Planned | Reliability | Install a TCR/FC at the Monocacy 230 kV bus to enable a smooth controlled VAR operation between a range of -150 MVAR to 50 MVAR
PJM | PA | 213453 | BUCKNGHM |  |  |  | 230 | - | 2017-12-31 | Planned | Reliability | 50 MVAR reactor at Buckingham 230 kV
PJM | PA | 200001 | ALBURTIS |  |  |  | 500 | - | 2016-05-31 | Planned | Reliability | 200 MVAR shunt reactor at Alburtis 500 kV
PJM | PA | 207968 | ELIM |  |  |  | 230 | - | 2016-05-31 | Planned | Reliability | 100 MVAR shunt reactor at Elimsport 230 kV
PJM | NJ | 216900 | ATHENIA |  |  |  | 230 | - | 2015-12-31 | Planned | Reliability | 100 MVAR reactor at Athenia 230 kV
PJM | NJ | 217100 | BERGEN |  |  |  | 230 | - | 2015-12-01 | Planned | Reliability | 50 MVAR reactor at Bergen 230 kV
PJM | NJ | 218231 | HUDSON_REAC |  |  |  | 230 | - | 2015-06-01 | Planned | Reliability | 50 MVAR reactor at Hudson 230 kV
PJM | NJ | 219884 | STANTER_REAC |  |  |  | 230 | - | 2014-12-01 | In-Service | Reliability | Two 50 MVAR reactors at Stanley Tce 230 kV
PJM | NJ | 216914 | WORANGE |  |  |  | 230 | - | 2015-10-01 | Planned | Reliability | 50 MVAR reactor at West Orange 230 kV
PJM | NJ | 218867 | ALDENE_REAC |  |  |  | 230 | - | 2015-10-01 | Planned | Reliability | 50 MVAR reactor at Aldene 230 kV
PJM | NJ | 219125 | CAMDEN |  |  |  | 230 | - | 2015-12-31 | Planned | Reliability | 150 MVAR reactor at Camden 230 kV
PJM | NJ | 217150 | LAWRENCE |  |  |  | 230 | - | 2015-12-31 | Planned | Reliability | 50 MVAR reactor at Lawrence 230 kV
PJM | NJ | 218227 | HINCHAV_REAC |  |  |  | 230 | - | 2015-12-31 | Planned | Reliability | 50 MVAR reactor at Hinchmans 230 kV
PJM | NJ | 219765 | BEAVERBK_REA |  |  |  | 230 | - | 2015-12-30 | Planned | Reliability | 50 MVAR reactor at Beaver Brook 230 kV
PJM | NJ | 219766 | COXSCRNR_REA |  |  |  | 230 | - | 2015-12-31 | Planned | Reliability | 50 MVAR reactor at Cox's Corner 230 kV
PJM | PA | 208113 | SUSQ | 207999 | JENK |  | 230 | 23.7 | 2018-06-01 | Planned | Reliability | Rebuild approximately 23.7 miles of the Susquehanna - Jenkins 230kV circuit. This replaces a temporary SPS that is already planned to mitigate the violation until this solution is implemented
PJM | NJ | 218311 | SEWAREN |  |  |  | 230 | - | 2016-06-01 | Planned | Reliability | Eliminate the Sewaren 138 kV bus by installing a new 230 kV bay at Sewaren 230 kV
PJM | NJ | 218400 | SEWAREN | 218314 | METUCHEN_1 |  | 138 | 9.7 | 2016-06-01 | Planned | Reliability | Convert the two 138 kV circuits from Sewaren – Metuchen to 230 kV circuits including Lafayette and Woodbridge substation
PJM | NJ | 218469 | METUCHEN |  |  |  | 230 | - | 2016-06-01 | Planned | Reliability | Reconfigure the Metuchen 230 kV station to accommodate the two converted circuits
PJM | MD | 224606 | DICKERSO |  |  |  | 230 | - | 2016-06-01 | Planned | Reliability | Add two 100 MVAR reactors at Dickerson Station H and two 100 MVAR reactors at Brighton 230 kV substation
PJM | PA | 208072 | SIEG FRA | 207973 | FRAC |  | 230 | 53 | 2018-05-31 | Planned | Reliability | Rebuild the Siegfried-Frackville 230 kV line
PJM | MD | 220980 | RAPHAEL | 221103 | JOPPA621 |  | 230/115 | 3 | 2017-06-01 | Planned | Reliability | Install a 230/115kV transformer at Raphael Rd and construct approximately 3 miles of 115kV line from Raphael Rd. to Joppatowne. Construct a 115kV three-breaker ring at Joppatowne to accommodate the ne
PJM | NJ | 228310 | CHURCHTN |  |  |  | 230/69 | - | 2017-06-01 | Planned | Reliability | Install second 230/69 kV transformer and 230 kV circuit breaker at Churchtown substation
PJM | VA | 314176 | 6HARMONY |  |  |  | 230 | - | 2015-05-01 | Planned | Reliability | Install a 230 kV 54 MVAR capacitor bank on the 2016 line at Harmony Village Substation
PJM | VA | 912221 | X4-039 | 314170 | 6COHMIL |  | 230 | 1.3 | 2015-05-30 | Planned | Reliability | Wreck and rebuild approximately 1.3 miles of existing 230 kV line between Cochran Mill - X4-039 Switching Station
PJM | VA | 314794 | 6DOOMS | 314854 | 6LEXNGT1 |  | 230 | 39 | 2016-05-31 | Planned | Reliability | Build a new 39 mile 230 kV transmission line from Dooms - Lexington on existing right-of-way
PJM | VA | 314052 | 6IDYLWOD | 313842 | 6SCOTTS_RUN |  | 230 | 4.5 |  | Planned | Reliability | Construct 230 kV OH line along existing Line #2035 corridor, approx. 2.4 miles from Idylwood - Dulles Toll Road (DTR) and 2.1 miles on new right-of-way along DTR to new Scott's Run Substation
PJM | PA | 235971 | 01SQUABHLLW |  |  |  | 230 | - | 2015-06-01 | Under Construction | Reliability | Install a 250 MVAR SVC at Squab Hollow 230 kV
PJM | PA | 235248 | 01SHINGL |  |  |  | 230 | - | 2018-06-01 | Planned | Reliability | Convert the Shingletown 230kV bus into a 6 breaker ring bus
PJM | PA | 235971 | 01SQUABHLLW |  |  |  | 230/138 | - | 2015-06-01 | Under Construction | Reliability | Install a new 230/138kV transformer at Squab Hollow 230kV substation. Loop the Forest - Elko 230 kV line into Squab Hollow. Loop the Brookville - Elko 138 kV line into Squab Hollow.
PJM | PA | 200654 | 26ERIE E |  |  |  | 230 | - | 2018-06-01 | Planned | Reliability | Install 75 MVAR capacitor at the Erie East 230 kV substation
PJM | MD | 223983 | CHALK230 | 292453 | T133TAP1 |  | 230 | 11.75 |  | Planned | Reliability | Upgrade the Chalk Point - T133TAP 230 kV Ck. 1 (23063) and Ckt. 2 (23065) to 1200 MVA ACCR
PJM | VA | 314913 | 8LOUDOUN | 314933 | 8BRAMBLETON |  | 500 | 6.75 | 2017-06-01 | Planned | Reliability | Build a 2nd Loudoun - Brambleton 500 kV line within the existing ROW. The Loudoun - Brambleton 230 kV line will be relocated as an underbuild on the new 500 kV line
PJM | PA | 208094 | STAN |  |  |  | 230 | - | 2017-11-30 | Planned | Reliability | Rebuild Stanton 230 kV yard
PJM | WV | 242517 | 05WYOMIN |  |  |  | 765 | - | 2015-03-31 | Planned | Reliability | Install a 300 MVAR shunt reactor at AEP's Wyoming 765 kV station
PJM | NJ | 217960 | BERGEN_345 | 217058 | MARION |  | 345 | 17.4 | 2016-06-01 | Planned | Reliability | Convert the Bergen - Marion 138 kV path to double circuit 345 kV and associated substation upgrades
PJM | NJ | 217058 | MARION | 216908 | BAYONNE |  | 345 | 7.87 | 2018-06-01 | Planned | Reliability | Convert the Marion - Bayonne "L" 138 kV circuit to 345 kV and any associated substation upgrades
PJM | NJ | 217058 | MARION | 216908 | BAYONNE |  | 345 | 7.87 | 2018-06-01 | Planned | Reliability | Convert the Marion - Bayonne "C" 138 kV circuit to 345 kV and any associated substation upgrades
PJM | NJ | 216993 | NORTHAV | 217869 | AIRPORT |  | 345 | 1.3 | 2018-06-01 | Planned | Reliability | Construct a new North Ave - Airport 345 kV circuit and any associated substation upgrades
PJM | NJ | 216993 | NORTHAV | 217958 | LINDEN_345 |  | 345 | 5.2 | 2018-06-01 | Planned | Reliability | Relocate the underground portion of North Ave - Linden "T" 138 kV circuit to Bayway, convert it to 345 kV, and any associated substation upgrades
PJM | NJ | 217869 | AIRPORT | 217134 | BAYWAY |  | 345 | 3.5 | 2018-06-01 | Planned | Reliability | Construct a new Airport - Bayway 345 kV circuit and any associated substation upgrades
PJM | NJ | 217958 | LINDEN_345 | 216993 | NORTHAV |  | 345 | 5.2 | 2018-06-01 | Planned | Reliability | Relocate the overhead portion of Linden - North Ave "T" 138 kV circuit to Bayway, convert it to 345 kV, and any associated substation upgrades
PJM | NJ | 217134 | BAYWAY | 217958 | LINDEN_345 |  | 345 | 2.5 | 2017-06-01 | Planned | Reliability | Convert the Bayway - Linden "Z" 138 kV circuit to 345 kV and any associated substation upgrades
PJM | NJ | 217178 | Q206_HUDSNDC |  |  |  | 345 | 20 | 2018-06-01 | Planned | Reliability | Relocate Farragut - Hudson "B" and "C" 345 kV circuits to Marion 345 kV and any associated substation upgrades
PJM | NJ | 217178 | Q206_HUDSNDC |  |  |  | 345 | - | 2016-06-01 | Planned | Reliability | Relocate the Hudson 2 generation to inject into the 345 kV at Marion and any associated upgrades
PJM | NJ | 217960 | BERGEN_345 |  |  |  | 345/230 | - | 2016-06-01 | Planned | Reliability | New Bergen 345/230 kV transformer and any associated substation upgrades
PJM | NJ | 217960 | BERGEN_345 |  |  |  | 345/138 | - | 2016-06-01 | Planned | Reliability | New Bergen 345/138 kV transformer #1 and any associated substation upgrades
PJM | NJ | 217134 | BAYWAY |  |  |  | 345/138 | - | 2017-06-01 | Planned | Reliability | New Bayway 345/138 kV transformer #1 and any associated substation upgrades
PJM | NJ | 217134 | BAYWAY |  |  |  | 345/138 | - | 2017-06-01 | Planned | Reliability | New Bayway 345/138 kV transformer #2 and any associated substation upgrades
PJM | NJ | 217958 | LINDEN_345 |  |  |  | 345/230 | - | 2017-06-01 | Planned | Reliability | New Linden 345/230 kV transformer and any associated substation upgrades
PJM | PA | 200568 | 26ERIE SO. |  |  |  | 230 | - | 2016-06-01 | Planned | Reliability | Install +250/-100 MVAR SVC at the Erie South 230 kV station
PJM | VA | 314041 | 6GLEBE | 226831 | STA_C_PAR |  | 230 | 2 |  | Planned | Reliability | Construct new underground 230 kV line from Glebe to Station C, rebuild Glebe Substation, construct 230 kV high-side bus at Station C with option to install 800 MVA PAR
NYISO | NY | 137200 | EDIC 345.00 | 130753 | FRASR345 345.00 | 1 | 345 | 76.3 | 2018 | Planned | Public Policy | Marcy South Series Compensation | Adds switchable series compensation to existing line
NYISO | NY | 130750 | COOPC345 345.00 | 130753 | FRASR345 345.00 | 1 | 345 | 46.64 | 2018 | Planned | Public Policy | Marcy South Series Compensation | Reconductor existing line and add switchable series compensation
NYISO | NY | 130750 | COOPC345 345.00 | 147833 | MARCY T1 345.00 | 1 | 345 | 134.9 | 2018 | Planned | Public Policy | Marcy South Series Compensation | Adds switchable series compensation to existing line
NYISO | NY | 125001 | ROCK TAV 345.00 | 126297 | RAMAPO 345.00 | 2 | 345 | 27.4 | 2018 | Planned | Public Policy | 2nd Rock Tavern - Ramapo 345 kV line
NYISO | NY | 126283 | GOTHLS N 345.00 | 126286 | GOWANUSN 345.00 | 1 | 345 | 12.95 | 2018 | Planned | Public Policy | Staten Island Un-bottling | Increase ratings on existing line
NYISO | NY | 126285 | GOTHLS S 345.00 | 126287 | GOWANUSS 345.00 | 1 | 345 | 12.95 | 2018 | Planned | Public Policy | Staten Island Un-bottling | Increase ratings on existing line
NYISO | NY | 126286 | GOWANUSN 345.00 | 126590 | GOWANUS 41SR345.00 | BY | 345 |  | 2018 | Planned | Public Policy | Staten Island Un-bottling | Increase ratings on existing line
NYISO | NY | 126286 | GOWANUSN 345.00 | 126590 | GOWANUS 41SR345.00 | SR | 345 |  | 2018 | Planned | Public Policy | Staten Island Un-bottling | Increase ratings on existing line
NYISO | NY | 126287 | GOWANUSS 345.00 | 126591 | GOWANUS 42SR345.00 | BY | 345 |  | 2018 | Planned | Public Policy | Staten Island Un-bottling | Increase ratings on existing line
NYISO | NY | 126287 | GOWANUSS 345.00 | 126591 | GOWANUS 42SR345.00 | SR | 345 |  | 2018 | Planned | Public Policy | Staten Island Un-bottling | Increase ratings on existing line
NYISO | NY | 126590 | GOWANUS 41SR345.00 | 126645 | FARRAGUT EAS345.00 | 1 | 345 | 4.05 | 2018 | Planned | Public Policy | Staten Island Un-bottling | Increase ratings on existing line
NYISO | NY | 126591 | GOWANUS 42SR345.00 | 126644 | FARRAGUT WES345.00 | 1 | 345 | 4.05 | 2018 | Planned | Public Policy | Staten Island Un-bottling | Increase ratings on existing line
TVA | TN | 360555 | Red Hill | 361661 | Hillsboro | 1 | 161 | 4.7 | 2013-11-01 | Completed | Reliability | New Line
TVA | AL | 360053 | Browns Ferry 1 | 360055 | Trinity | 1 | 161 | 10.9 | 2013-11-01 | Completed | Reliability | Upgrade Line
TVA | AL | 360271 | Athens (AL) | 360271 | Athens (AL) | 1 | 161 | N/A | 2013-11-01 | Completed | Reliability | New Capacitor Bank
TVA | AL | 360263 | Wilson Hydro | 361697 | Jackson Avenue | 1 | 161 | 4.3 | 2013-11-01 | Completed | Reliability | Tap Wilson-Caddo
TVA | KY | 360336 | Franklin (KY) | 361690 | North Franklin | 1 | 161 | 1.6 | 2013-11-01 | Completed | Reliability | Tap Franklin-Woodburn
TVA | KY | 361699 | Beulah Grove Tap | 361700 | Beulah Grove | 1 | 161 | 2.5 | 2013-11-01 | Completed | Reliability | Tap McGregors Chapel-Pontotoc
TVA | AL | 361098 | Solutia | 361692 | Toray | 1 | 161 | 0.1 | 2013-11-01 | Completed | Reliability | Tap Solutia-Ratliff
TVA | TN | 360071 | Wilson | 360581 | Pin Hook | 1 | 500 | 14.2 | 2013-11-01 | Completed | Reliability | Upgrade Line
TVA | AL/TN | 360260 | Colbert | 361298 | Waynesboro Tap | 1 | 161 | 25.6 | 2013-11-01 | Completed | Reliability | Upgrade Line
TVA | KY | 361677 | Salem Church Tap | 361678 | Salem Church | 1 | 161 | 4.7 | 2013-11-01 | Completed | Reliability | Tap Edgoten-Commerce Park
MISO/TVA | KY | 340624 | Paradise Tap | 360043 | Paradise | 1 | 161 | 8 | 2014-04-01 | Completed | Reliability | Upgrade Interconnection
TVA | AL | 360279 | Guntersville | 361481 | Brindley | 1 | 161 | 11.2 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | TN | 360391 | Fayetteville | 360392 | Winchester | 1 | 161 | 28.2 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | TN | 361680 | Waynesboro City | 361687 | Waynesboro City Tap | 1 | 161 | 5 | 2014-06-01 | Completed | Reliability | Tap Hohenwald-Waynesboro
TVA | TN | 361143 | Collierville (MS) | 361691 | Wingo Road | 1 | 161 | 1 | 2014-06-01 | Completed | Reliability | Construct Wingo Road, Tap Collierville-Rossville
TVA | TN | 361795 | Piperton | 361691 | Wingo Road | 1 | 161 | 3 | 2014-06-01 | Completed | Reliability | Construct Wingo Road, Tap Collierville-Rossville
TVA | TN | 360359 | South Nashville | 365203 | Trinity Hills (NES) | 1 | 161 | 8 | 2014-06-01 | Completed | Reliability | Construct Trinity Hills, Tap South Nashville-West Nashville
TVA | TN | 360360 | West Nashville | 365203 | Trinity Hills (NES) | 1 | 161 | 6.3 | 2014-06-01 | Completed | Reliability | Construct Trinity Hills, Tap South Nashville-West Nashville
TVA | MS | 360036 | West Point | 361682 | Waverly | 1 | 161 | 5.3 | 2014-06-01 | Completed | Reliability | Construct Waverly, Tap West Point-West Columbus
TVA | MS | 360525 | West Columbus | 361682 | Waverly | 1 | 161 | 10.1 | 2014-06-01 | Completed | Reliability | Construct Waverly, Tap West Point-West Columbus
TVA | TN | 360101 | John Sevier 2 | 361061 | Greenville Tap 1 | 1 | 161 | 8.5 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | KY | 360016 | Marshall | 360496 | C-33 (DOE) | 1 | 161 | 30.2 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | TN | 360101 | John Sevier 2 | 361551 | Pioneer Tap | 1 | 161 | 16.6 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | AL | 361066 | Priceville Tap | 361217 | Pence Tap | 1 | 161 | 8.2 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | AL | 360276 | Decatur | 361066 | Priceville Tap | 1 | 161 | 7.2 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | AL/TN | 360274 | Ardmore | 361598 | Park City Tap | 1 | 161 | 17.3 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | AL | 360271 | Athens (AL) | 360274 | Ardmore | 1 | 161 | 10.3 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | AL | 360271 | Athens (AL) | 360532 | Browns Ferry 2 | 1 | 161 | 14.3 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | AL | 361150 | Laceys Spring Tap | 361481 | Brindley | 1 | 161 | 3.4 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | KY | 360130 | Mayfield | 361480 | Golo | 1 | 161 | 6.4 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | TN | 360420 | East Cleveland | 361439 | Benton (TN) | 1 | 161 | 10.2 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | TN | 360424 | Apalachia | 361439 | Benton (TN) | 1 | 161 | 12.4 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | MS | 360036 | West Point | 361529 | Starkville SS | 1 | 161 | 14.2 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | AL | 360268 | Elgin | 361703 | Lexington (AL) | 1 | 161 | 8.2 | 2014-06-02 | Completed | Reliability | Construct Lexington, Tap Elgin-Dunn
TVA | AL | 360502 | Dunn | 361703 | Lexington (AL) | 1 | 161 | 16.3 | 2014-06-01 | Completed | Reliability | Construct Lexington, Tap Elgin-Dunn
TVA | TN | 360100 | John Sevier 1 | 360100 | John Sevier 1 | 1 | 161 | N/A | 2014-06-01 | Completed | Reliability | Reconfigure Yard
TVA | AL | 360059 | East Point | 361350 | Fairview Tap | 1 | 161 | 10.6 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | AL | 360277 | Arab | 361350 | Fairview Tap | 1 | 161 | 13 | 2014-06-01 | Completed | Reliability | Upgrade Line
TVA | MS | 360033 | Union | 360734 | Union 2 (Transformer) | 2 | 500/161 | N/A | 2014-06-01 | Completed | Reliability | Install Transformer
TVA | KY/TN | 360160 | Dover | 360326 | Barkley | 1 | 161 | 48.5 | 2014-11-01 | Under Construction | Reliability | Upgrade Line
TVA | AL | 360282 | Collinsville | 361679 | Geraldine | 1 | 161 | 11.9 | 2014-11-01 | Under Construction | Reliability | Construct Geraldin,Tap Collinsville-Albertville
TVA | AL | 360283 | Albertville | 361679 | Geraldine | 1 | 161 | 12.6 | 2014-11-01 | Under Construction | Reliability | Construct Geraldin,Tap Collinsville-Albertville
TVA | TN | 361088 | Rossville Tap | 361795 | Piperton | 1 | 161 | 1.4 | 2014-11-01 | Under Construction | Reliability | Construct Piperton, Tap Wingo Road-Rossville
TVA | TN | 361691 | Wingo Road | 361795 | Piperton | 1 | 161 | 3 | 2014-11-01 | Under Construction | Reliability | Construct Piperton, Tap Wingo Road-Rossville
TVA | TN | 360471 | Tusculum | 361551 | Pioneer Tap | 1 | 161 | 2 | 2014-11-01 | Under Construction | Reliability | Upgrade Line
TVA | TN | 360101 | John Sevier 2 | 360471 | Tusculum | 2 | 161 | 18.7 | 2014-11-01 | Under Construction | Reliability | New Line
TVA | TN | 360471 | Tusculum | 361468 | Walters (JCPB) | 1 | 161 | 15 | 2014-11-01 | Under Construction | Reliability | New Line
TVA | TN | 360151 | Ripley (TN) | 361441 | Curve | 1 | 161 | 5.4 | 2014-11-01 | Under Construction | Reliability | New Line
TVA | TN | 360151 | Ripley (TN) | 361216 | East Industrial Park Tap | 1 | 161 | 3.8 | 2014-11-01 | Under Construction | Reliability | New Line
TVA | TN | 360147 | Huntingdon | 360514 | Holladay | 1 | 161 | 20.3 | 2014-11-01 | Under Construction | Reliability | New Line
TVA | TN | 360146 | Milan | 360147 | Huntingdon | 1 | 161 | 30 | 2014-11-01 | Under Construction | Reliability | New Line
TVA | AL | 360656 | Madison 2 | 361681 | Charity Lane | 1 | 161 | 13.6 | 2014-11-01 | Under Construction | Reliability | New Line
TVA | TN | 361796 | Cornersville Tap | 361797 | Cornersville | 1 | 161 | 4 | 2014-11-01 | Under Construction | Reliability | Tap Elk Ridge-Collins Creek
TVA | TN | 360725 | Freeport 2 | 365788 | Mendenhall Road, Sub 89 (MLGW) | 1 | 161 | 11.8 | 2014-11-01 | Under Construction | Reliability | Construct Mendenhall,Tap Freeport-Clarke Road
TVA | TN | 365719 | Clarke Road, Sub 71 (MLGW) | 365788 | Mendenhall Road, Sub 89 (MLGW) | 1 | 161 | 11.9 | 2014-11-01 | Under Construction | Reliability | Construct Mendenhall,Tap Freeport-Clarke Road
TVA | TN | 361277 | Goodfield Tap | 361696 | Georgetown Tap | 1 | 161 | 15.3 | 2014-11-01 | Under Construction | Reliability | Tap Sequoyah-Goodfield
TVA | TN | 360460 | Nixon Road | 360527 | East Knox | 1 | 161 | 11.1 | 2015-06-01 | Planned | Reliability | Construct East Knox, Tap Dumplin Valley-Nixon Road
TVA | TN | 360133 | Dumplin Valley | 360527 | East Knox | 1 | 161 | 7.8 | 2015-06-01 | Planned | Reliability | Construct East Knox, Tap Dumplin Valley-Nixon Road
TVA | TN | 360098 | Volunteer 1 | 360527 | East Knox | 1 | 161 | 13 | 2015-06-01 | Planned | Reliability | New Line
TVA | TN | 360038 | Johnsonville Fossil 1-4 | 360038 | Johnsonville Fossil 1-4 | 1 | 161 | N/A | 2015-06-01 | Planned | Reliability | New Capacitor Bank
TVA | TN | 360424 | Apalachia | 360658 | Northeast Benton | 1 | 161 | 11.2 | 2015-06-01 | Planned | Reliability | Upgrade Line
TVA | TN | 360420 | East Cleveland | 360658 | Northeast Benton | 1 | 161 | 13.8 | 2015-06-01 | Planned | Reliability | Upgrade Line
TVA | TN | 360152 | South Jackson | 361704 | Flex Drive | 1 | 161 | 4.1 | 2015-06-01 | Planned | Reliability | Construct Flex Drive,Tap South Jackson-Alumax
TVA | TN | 361030 | Alumax Tap | 361704 | Flex Drive | 1 | 161 | 3.2 | 2015-06-01 | Planned | Reliability | Construct Flex Drive,Tap South Jackson-Alumax
TVA | TN | 361694 | South Pittsburg Tap | 361695 | South Pittsburg | 1 | 161 | 5 | 2015-06-01 | Planned | Reliability | Tap Tennol-Tennol Tap
TVA | TN | 360173 | North Lexington | 361594 | Lexington (TN) | 1 | 161 | 3.8 | 2015-06-01 | Planned | Reliability | Construct Lexington,Tap North Lexington-West Lexington
TVA | TN | 361319 | West Lexington | 361594 | Lexington (TN) | 1 | 161 | 0.8 | 2015-06-01 | Planned | Reliability | Construct Lexington,Tap North Lexington-West Lexington
TVA | TN | 360640 | Johnsonville | 360640 | Johnsonville | 1 | 161 | N/A | 2017-06-01 | Planned | Reliability | Reconfigure Yard
TVA | TN | 360071 | Wilson | 360077 | Plateau | 1 | 500 | 75.6 | 2018-11-01 | Planned | Reliability | Construct Plateau 500kV, Loop Roane-Wilson
TVA | TN | 360090 | Roane | 360077 | Plateau | 1 | 500 | 49.2 | 2018-11-01 | Planned | Reliability | Construct Plateau 500kV, Loop Roane-Wilson
TVA | TN | 361237 | Monterey | 360078 | Plateau | 1 | 161 | 6.1 | 2018-11-01 | Planned | Reliability | Construct Plateau 161kV, Loop Monterey-Campbell Junction
TVA | TN | 361417 | Campbell Junction | 360078 | Plateau | 1 | 161 | 3.2 | 2018-11-01 | Planned | Reliability | Construct Plateau 161kV, Loop Monterey-Campbell Junction
TVA | TN | 360077 | Plateau | 360078 | Plateau | 1 | 500/161 | N/A | 2018-11-01 | Planned | Reliability | Install Transformer
TVA | TN | 360678 | Shelby (MLGW) 1 | 365573 | Bolen Huse Road, Sub 75 (MLGW) | 1 | 161 | 5.8 | 2019-11-01 | Planned | Reliability | Construct Bolen Huse Road, Tap Shelby-NE Gate
TVA | TN | 365591 | Northeast Gate, Sub 33 (MLGW) | 365573 | Bolen Huse Road, Sub 75 (MLGW) | 1 | 161 | 9.8 | 2019-11-01 | Planned | Reliability | Construct Bolen Huse Road, Tap Shelby-NE Gate
TVA | MS | 365826 | Collierville Gate, Sub 86 (MLGW) | 365913 | South Collierville, Sub 83 (MLGW) | 1 | 161 | 5.6 | 2018-11-01 | Planned | Reliability | Construct S Collierville, Tap Shelton Road-Collgate
TVA | MS | 365827 | Shelton Road, Sub 79 (MLGW) | 365913 | South Collierville, Sub 83 (MLGW) | 1 | 161 | 5.6 | 2018-11-01 | Planned | Reliability | Construct S Collierville, Tap Shelton Road-Collgate