## 2025_Summer
Source |  | Sink |  | Comments | FCITC (MW) | Limiting PA | Limiting Facility | Rating (MVA) | TDF (%) | Cont.PA | Contingency / Outaged Facility | Operating Guide
A | FRCC | E | SERC |  | 343.1 | DEF-SEC | 403528 MARTIN WEST 230 407120 SLV_SP_N 230 1 | 384 | -0.09138 | DEF | 403173 BRONSON DUKE 230 403522 CRYST RVR PL 230 1
[5 empty] | 1186.7 | DEF | 403173 BRONSON DUKE 230 403522 CRYST RVR PL 230 1 | 476 | -0.07765 | NA | Base Case
[5 empty] | 1678.8 | DEF | 403528 MARTIN WEST 230 403530 WILLISTON 230 1 | 436 | 0.09436 | DEF | 403173 BRONSON DUKE 230 403522 CRYST RVR PL 230 1
[5 empty] | 1727.2 | DEF | 403173 BRONSON DUKE 230 403522 CRYST RVR PL 230 1 | 575 | -0.08674 | DEF | 403521 CENTRAL FLA 230 403525 DALLAS 230 1
[5 empty] | 2566.6 | DEF | 403159 ARCHER 230 403530 WILLISTON 230 1 | 436 | -0.08761 | DEF | 403165 NEWBERRY 230 403173 BRONSON DUKE 230 1
[5 empty] | 2826.8 | FPL | 400375 BALDWIN 115 400406 MACLENNY 115 1 | 239 | 0.04001 | SOCO-FPL | 380015 8THALMANN 500 400356 DUVAL 500 1
B | MISO | C | NPCC | A base transfer of 1800 MW from MISO-NPCC is already modeled into this basecase.This 1800 MW is already included in the FCITC values presented in the next column. | 674.4 | NYISO | 126294 PLTVLLEY 345 137451 LEEDS 3 345 2 | 1538 | -0.09245 | NYISO | SB:PV345_RNS4 | SPS
[5 empty] | 812.6 | NYISO | 126294 PLTVLLEY 345 137455 ATHENS 345 1 | 1538 | -0.09117 | NYISO | SB:LEEDS345_R92 | SPS
[5 empty] | 1557.5 | NYISO | 126294 PLTVLLEY 345 137451 LEEDS 3 345 2 | 1538 | -0.09368 | NYISO | SB:AT_R9162 | SPS
[5 empty] | 1716.5 | NYISO | 130836 N.WAV115 115 131018 LOUNS115 115 1 | 131 | 0.07839 | NYISO | SB:Oakd345_36-3122_no-sps | Operating Procedure
[5 empty] | 1779.7 | NYISO | 131018 LOUNS115 115 131850 CNYOG115 115 1 | 131 | 0.07839 | NYISO | SB:Oakd345_36-3122_no-sps | Operating Procedure
[5 empty] | 1807.5 | NYISO | 130848 S.OWE115 115 131850 CNYOG115 115 1 | 131 | -0.07839 | NYISO | SB:Oakd345_36-3122_no-sps | Operating Procedure
[5 empty] | 1999 | NYISO | 130836 N.WAV115 115 200676 26E.SAYRE 115 1 | 128 | -0.11274 | NYISO | SB:HILL_B412 | Operating Procedure
[5 empty] | 2182.9 | PJM | 200674 26TOWANDA 115 200676 26E.SAYRE 115 1 | 191 | 0.11274 | NYISO | SB:HILL_B412
[5 empty] | 2308.7 | NYISO | 130836 N.WAV115 115 131018 LOUNS115 115 1 | 131 | 0.07712 | NYISO | SB:OAKD345_31-B322 | Operating Procedure
[5 empty] | 2406.6 | NYISO | 130848 S.OWE115 115 130932 GOUDEY8-115 115 1 | 131 | 0.07839 | NYISO | SB:Oakd345_36-3122_no-sps | Operating Procedure
[5 empty] | 2592.1 | NYISO-PJM | 130836 N.WAV115 115 200676 26E.SAYRE 115 1 | 108 | -0.06776 | NYISO | Base Case | Operating Procedure
[5 empty] | 2860.2 | NYISO | 130787 CODNT115 115 130830 MONTR115 115 1 | 128 | -0.05975 | NYISO | SB:OAKD345_31-B322 | Operate to STE
[5 empty] | 2926.2 | NYISO | 130765 OAKDL230 230 130772 SHRED230 230 1 | 400 | -0.13764 | NYISO | SB:Oakd345_36-3122_no-sps
[5 empty] | 2986.3 | PJM | 200678 26LENOX 115 200936 26WILLMS 115 1 | 134 | 0.05584 | NYISO | Base Case
[5 empty] | 3004.9 | PJM | 200677 26NO MESHO 115 200678 26LENOX 115 1 | 189 | 0.0697 | NYISO | SB:Oakd345_36-3122_no-sps
[5 empty] | 3016.6 | NYISO | 130848 S.OWE115 115 130932 GOUDEY8-115 115 1 | 131 | 0.07979 | NYISO | SB:WATRC345_31-2 | Operate to STE
[5 empty] | 3121.6 | NYISO-PJM | 130807 WESTOVER115 115 200680 26LAUREL L 115 1 | 128 | -0.0697 | NYISO | SB:Oakd345_36-3122_no-sps | Operating Procedure
[5 empty] | 3185 | NYISO-PJM | 130763 HILSD230 230 200675 26E.TWANDA 230 1 | 531 | -0.23963 | NYISO | R:EESR/WF/NWES
[5 empty] | 3246.3 | NYISO | 130750 COOPC345 345 146754 MDTN TAP 345 1 | 1793 | 0.15516 | NYISO | SB:ROCK345_4255
[5 empty] | 3276.8 | NYISO-PJM | 130763 HILSD230 230 200675 26E.TWANDA 230 1 | 483 | -0.19035 | NYISO | Base Case
[5 empty] | 3544.6 | NYISO | 130750 COOPC345 345 146754 MDTN TAP 345 1 | 1793 | 0.15195 | NYISO | SB:ROCK345_376512_UC27
[5 empty] | 3853.2 | NYISO | 137451 LEEDS 3 345 147831 GILB 345 345 1 | 1605 | -0.14002 | NYISO | T:34&42B_CE18/UC30
[5 empty] | 4015.5 | NYISO-PJM | 135277 FALCONER 115 200579 26WARREN 115 1 | 116 | -0.05786 | NYISO | SB:MASS_765_7102
B | MISO | D | PJM |  | 4419.3 | AMIL | 346809 7CASEY 345 347830 7NEWTON 345 1 | 1200 | -0.03806 | NA | Base Case
B | MISO | E | SERC |  | NO LIMIT
B | MISO | F | SPP |  | 404.1 | EES-EAI | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | 396 | 0.06601 | EES-EAI | 337909 8ANO% 500 515305 FTSMITH8 500 1
[5 empty] | 430.6 | EES-EAI | 337904 5RUSSELVL.S 161 337905 5RUSSELVL.E! 161 1 | 446 | -0.06601 | EES-EAI | 337909 8ANO% 500 515305 FTSMITH8 500 1
[5 empty] | 585.9 | EES-EAI | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 450 | -0.04399 | EES-EAI | 337909 8ANO% 500 515305 FTSMITH8 500 1
[5 empty] | 1290.2 | EES-EAI | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | 518 | -0.04399 | EES-EAI | 337909 8ANO% 500 515305 FTSMITH8 500 1
[5 empty] | 2540.1 | EES-EAI - OKGE | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 1299 | 0.1136 | WERE | 532751 WCGS U1 25.0 532797 WOLFCRK7 345 1
[5 empty] | 4003.9 | EES-EAI-AEPW | 337902 5DANVLE AR! 161 507195 MAGZREC5 161 1 | 335 | 0.03101 | EES-EAI | 337909 8ANO% 500 515305 FTSMITH8 500 1
C | NPCC | B | MISO | A base transfer of 1800 MW from NPCC-MISO is already modeled into this basecase.This 1800 MW is already included in the FCITC values presented in the next column. | 1969 | NYISO | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | 275 | -0.03795 | NYISO | T:61&191 | Operate to STE
[5 empty] | 2047.8 | NYISO | 126561 8E DUM 138 126643 RAINEY EAST 345 8 | 305 | 0.04505 | NYISO | SB:RAIN345_8W | Operating Exception
[5 empty] | 2178.3 | NYISO | 130807 WESTOVER115 115 130838 OAKDL115 115 1 | 274 | -0.09408 | NYISO | T:34&42B_CE18/UC30 | Operating Procedure
[5 empty] | 2258.7 | NYISO | 130807 WESTOVER115 115 130838 OAKDL115 115 1 | 238 | -0.09994 | NYISO | Base Case | Operating Procedure
[5 empty] | 2417.7 | NYISO | 126561 8E DUM 138 126643 RAINEY EAST 345 8 | 252 | 0.03538 | NYISO | Base Case | Operating Exception
[5 empty] | 2543.6 | NYISO | 135450 GRDNVL1 115 135453 LONG-180 115 1 | 166 | -0.04631 | NYISO | T:79&80 | Operate to STE
[5 empty] | 2708.5 | NYISO | 136150 CLAY 345 136156 VOLNEY 345 1 | 1344 | -0.05043 | NYISO | SB:OSWE_R985
[5 empty] | 2911.5 | NYISO | 130794 DELHI115 115 130804 DEL T115 115 1 | 164 | -0.03478 | NYISO | SB:LAFA_ELB
[5 empty] | 3040.4 | NYISO | 130787 CODNT115 115 130830 MONTR115 115 1 | 128 | 0.06087 | NYISO | SB:Oakd345_36-3122_no-sps
[5 empty] | 3145 | NYISO | 130807 WESTOVER115 115 200680 26LAUREL L 115 1 | 128 | 0.06887 | NYISO | SB:OAKD345_31-B322
[5 empty] | 3232.7 | NYISO | 135251 S RIPLEY 230 200654 26ERIE E 230 1 | 607 | 0.21141 | NYISO | T:34&42B_CE18/UC30
[5 empty] | 3300.9 | NYISO | 135251 S RIPLEY 230 200654 26ERIE E 230 1 | 607 | 0.21975 | NYISO | SB:Oakd345_36-3122_no-sps
[5 empty] | 3429 | NYISO | 130776 BORDR115 115 130823 GUARD115 115 1 | 179 | 0.03532 | NYISO | SB:LAFAYETT
C | NPCC | D | PJM | A base transfer of 1600 MW from NPCC-PJM is already modeled into this basecase.This 1600 MW is already included in the FCITC values presented in the next column. | 759.542 | NYISO | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | 275 | -0.03708 | NYISO | T:61&191 | Operate to STE
[5 empty] | -204.2 | NYISO | 126561 8E DUM 138 126643 RAINEY EAST 345 8 | 305 | 0.04209 | NYISO | SB:RAIN345_8W | Operating Exception
[5 empty] | 1177.52 | NYISO | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 166 | -0.04818 | NYISO | T:79&80 | Operate to STE
[5 empty] | 1254.4216 | NYISO | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 166 | -0.04993 | NYISO | T:77&78 | Operate to STE
[5 empty] | 802.5 | NYISO | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | 444 | 0.2028 | NYISO | T:34&42B_CE18/UC30
[5 empty] | 918.6 | NYISO | 135450 GRDNVL1 115 135453 LONG-180 115 1 | 166 | -0.04755 | NYISO | T:77&78 | Operate to STE
[5 empty] | 1030.5 | NYISO | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | 444 | 0.20766 | NYISO | Base Case
[5 empty] | 1113.6 | NYISO | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 181 | 0.04648 | NYISO | T:79&80
[5 empty] | 1209.4 | NYISO | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 181 | 0.04862 | NYISO | T:77&78
[5 empty] | 1305 | NYISO-PJM | 135251 S RIPLEY 230 200654 26ERIE E 230 1 | 501 | 0.20766 | NYISO | Base Case
[5 empty] | 1411.7 | NYISO | 135443 ECWA-182 115 135459 NI.B-182 115 1 | 181 | -0.04664 | NYISO | T:79&80
[5 empty] | 1502 | NYISO | 135450 GRDNVL1 115 135475 S139-141 115 1 | 101 | 0.0573 | NYISO | T:73&74
[5 empty] | 1512.6 | NYISO | 135443 ECWA-182 115 135496 YNG-182 115 1 | 181 | 0.04891 | NYISO | T:77&78
D | PJM | B | MISO |  | 5298.8 | CE | 270864 QUAD 1 3-11 345 631141 ROCK CK3 345 1 | 999 | 0.03246 | NA | Base Case
D | PJM | C | NPCC | A base transfer of 3000 MW from PJM-NPCC is already modeled into this basecase.This 3000 MW is already included in the FCITC values presented in the next column. | -1895 | NYISO | 126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 962 | 0.05873 | NYISO | SB:SPRA345_RNS2 | Operate to STE
[5 empty] | 1630.3 | PJM | 200674 26TOWANDA 115 200675 26E.TWANDA 230 4 | 226 | -0.05371 | NYISO | R:C398/NWES
[5 empty] | 1829.8 | NYISO | 130836 N.WAV115 115 200676 26E.SAYRE 115 1 | 128 | -0.11655 | NYISO | SB:HILL_B312 | Operating Procedure
[5 empty] | 1943.6 | NYISO | 130836 N.WAV115 115 200676 26E.SAYRE 115 1 | 128 | -0.1176 | NYISO | SB:HILL_B412 | Operating Procedure
[5 empty] | 2051.1 | NYISO | 130836 N.WAV115 115 131018 LOUNS115 115 1 | 131 | 0.07951 | NYISO | SB:Oakd345_36-3122_no-sps | Operating Procedure
[5 empty] | 2131.7 | NYISO | 131018 LOUNS115 115 131850 CNYOG115 115 1 | 131 | 0.07951 | NYISO | SB:Oakd345_36-3122_no-sps | Operating Procedure
[5 empty] | 2426.2 | PJM | 200678 26LENOX 115 200936 26WILLMS 115 1 | 162 | 0.08984 | NYISO | R:C398/NWES
[5 empty] | 2525.1 | NYISO | 130836 N.WAV115 115 131018 LOUNS115 115 1 | 131 | 0.08109 | NYISO | SB:WATRC345_31-2 | Operating Procedure
[5 empty] | 2600.4 | PJM | 200677 26NO MESHO 115 200678 26LENOX 115 1 | 189 | 0.09385 | NYISO | R:C398/NWES
[5 empty] | 2726.3 | PJM | 200677 26NO MESHO 115 200678 26LENOX 115 1 | 189 | 0.09456 | NYISO | R:ETHS/NWES
[5 empty] | 2806.5 | NYISO | 130807 WESTOVER115 115 200680 26LAUREL L 115 1 | 128 | -0.09396 | NYISO | R:C398/NWES | Operating Procedure
[5 empty] | 2903.1 | NYISO | 126294 PLTVLLEY 345 137455 ATHENS 345 1 | 1538 | -0.09097 | NYISO | SB:LEEDS345_R92 | SPS
[5 empty] | 2944.9 | PJM | 200677 26NO MESHO 115 200678 26LENOX 115 1 | 136 | 0.06067 | NYISO | Base Case
D | MISO | E | SERC |  | NO ADDITIONAL LIMIT
E | SERC | A | FRCC |  | 2356 | FPL | 400398 HUDSONFL 230 407119 SEMINOLE 230 1 | 637 | -0.08174 | FPL | 400477 RICE 500 400484 ROBERTS 500 1
[5 empty] | 2529.4 | SOCO | 380015 8THALMANN 500 400356 DUVAL 500 1 | 2598 | 0.66598 | SOCO | 380014 8HATCH 500 400356 DUVAL 500 1
[5 empty] | 2674.9 | SOCO | 382148 3HOMELAND 115 382149 3STGEORGE 115 1 | 124 | 0.03207 | SOCO | 380015 8THALMANN 500 400356 DUVAL 500 1
[5 empty] | 2781.1 | SOCO | 380014 8HATCH 500 400356 DUVAL 500 1 | 2598 | 0.60919 | SOCO | 380015 8THALMANN 500 400356 DUVAL 500 1
[5 empty] | 2958.8 | FPL | 400468 PUTNAM 230 401099 RICEBYPASS 230 1 | 588 | -0.09525 | SOCO | 400477 RICE 500 400484 ROBERTS 500 1
[5 empty] | 3011 | DEF | 403162 FT WHITE N 230 403169 SUWANNEE RV 230 1 | 463 | -0.12906 | SOCO | 380015 8THALMANN 500 400356 DUVAL 500 1
E | SERC | B | MISO |  | 5494 | AMIL/EEI | 347325 7JOPPA TS 345 351003 5JOPPA TS 161 1 | 600 | -0.03423 | TVA | 360001 8SHAWNEE FP 500 360002 7SHAWNEE FP 345 11
E | SERC | D | PJM |  | 4336.6 | DVP | 346809 7CASEY 345 347830 7NEWTON 345 1 | 1200 | -0.03897 | NA | BASECASE
E | SERC | F | SPP |  | 336.3 | EES-EAI | 337904 5RUSSELVL.S 161 505508 DARDANE5 161 1 | 396 | 0.07933 | EES-MISO - OKGE-SPP | 337909 8ANO% 500 515305 FTSMITH8 500 1
[5 empty] | 358.3 | EES-EAI | 337904 5RUSSELVL.S 161 337905 5RUSSELVL.E! 161 1 | 446 | -0.07933 | EES-MISO - OKGE-SPP | 337909 8ANO% 500 515305 FTSMITH8 500 1
[5 empty] | 492.9 | EES-EAI | 337905 5RUSSELVL.E! 161 337906 5RUSSELVL.N 161 1 | 450 | -0.0523 | EES-MISO - OKGE-SPP | 337909 8ANO% 500 515305 FTSMITH8 500 1
[5 empty] | 1085.3 | EES-EAI | 337906 5RUSSELVL.N 161 337912 5ANO% 161 1 | 518 | -0.0523 | EES-MISO - OKGE-SPP | 337909 8ANO% 500 515305 FTSMITH8 500 1
[5 empty] | 2058.7 | EES-EAI | 337909 8ANO% 500 515305 FTSMITH8 500 1 | 1299 | 0.14016 | SPP | 532751 WCGS U1 25.0 532797 WOLFCRK7 345 1
[5 empty] | 3218 | EES-EAI | 337902 5DANVLE AR! 161 507195 MAGZREC5 161 1 | 335 | 0.03858 | EES-MISO - OKGE-SPP | 337909 8ANO% 500 515305 FTSMITH8 500 1
F | SPP | B | MISO |  | 926.5 | OPPD | 645456 S3456 3 345 645458 S3458 3 345 1 | 956 | -0.05768 | OPPD | 645455 S3455 3 345 645740 S3740 3 345 1
[5 empty] | 1694.3 | OPPD | 645455 S3455 3 345 645740 S3740 3 345 1 | 1073 | -0.05201 | OPPD | 645456 S3456 3 345 645458 S3458 3 345 1
[5 empty] | 4284.1 | WERE | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1076 | -0.04935 | WERE | 532851 AUBURN 6 230 532852 JEC 6 230 1
[5 empty] | 4576.1 | WERE | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1076 | -0.0438 | WERE | 532766 JEC N 7 345 532767 GEARY 7 345 1
[5 empty] | 4856.1 | WERE | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1076 | -0.04579 | WERE | 532766 JEC N 7 345 532770 MORRIS 7 345 1
F | SPP | E | SERC |  | 1397 | OPPD | 645456 S3456 3 345 645458 S3458 3 345 1 | 956 | -0.03825 | OPPD | 645455 S3455 3 345 645740 S3740 3 345 1
[5 empty] | 2497.4 | OPPD | 645455 S3455 3 345 645740 S3740 3 345 1 | 1073 | -0.03529 | OPPD | 645456 S3456 3 345 645458 S3458 3 345 1
[5 empty] | 4475.8 | SWPA | 505502 TRUMAN 5 161 541314 NWARSAW5 161 1 | 223 | 0.03053 | AMMO | 345408 7OVERTON 345 541201 SIBLEY 7 345 1
[5 empty] | 4836.8 | WERE | 532765 HOYT 7 345 532766 JEC N 7 345 1 | 1076 | -0.04371 | WERE | 532851 AUBURN 6 230 532852 JEC 6 230 1