## Sheet1
FROM | TO | Description
AZ_NM_SNV | SPP_S | Ties with AZ_NM_SW were determined as the combined maximum capacity of the DC ties.
ENTERGY | MISO_MO_IL | To obtain the MRM-NEEM Pipe Transfer Limit between MISO and Entergy, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between MISO and Entergy. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies.
ENTERGY | SOCO | To obtain the MRM-NEEM Pipe Transfer Limit between Southern Company and Entergy, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between Southern Company and Entergy. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies performed in SERC.
ENTERGY | SPP_N | To obtain the MRN-NEEM Pipe Transfer Limit between SPP and Entergy, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then coordinated between SPP and Entergy.
ENTERGY | SPP_S | To obtain the MRN-NEEM Pipe Transfer Limit between SPP and Entergy, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then coordinated between SPP and Entergy.
ENTERGY | TVA | To obtain the MRM-NEEM Pipe Transfer Limit between TVA and Entergy, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between TVA and Entergy. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies.
ERCOT | SPP_S | Ties with ERCOT were determined as the combined maximum capacity of the DC ties.
FRCC | SOCO | The transfer capabilties provided as input in the MRN-NEEM model were obtained from the most recent FRCC - Southern joint TTC study. Their are no transmission enhancements that are currently planned that would increase the transfer capability between these regions.
MAPP_CA | MAPP_US | This value is the current Saskatchewan to MAPP_US operating limit plus the current MH to US operating limit, reduced by the value reported for "MAPP_CA to MISO_W".
MAPP_CA | MISO_W | This is part of the MH to US stability limited interface. This value is the current operating limit, reduced by 200 MW, which is included in the value for "MAPP_CA to MAPP_US".
MAPP_CA | IESO | This is the current MH to IESO operating limit as reported by IESO.
MAPP_US | MAPP_CA | This is the current MAPP_US to MAPP_CA operating limit on this single element tie line as reported by MH.
MAPP_US | MISO_W | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using PSS® MUST version 8.3.2.
MAPP_US | NE | The values for the pipe from "MAPP US" to "NE" are found using transfer study from generation to generation.
MAPP_US | NWPP | This is a DC tie to WECC. This value is the current operating limit for the DC tie.
MAPP_US | RMPA | This is a DC tie to WECC. This value is the current operating limit for the DC tie.
MISO_IN | MISO_MI | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_IN | MISO_MO_IL | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_IN | Non_RTO_Midwest | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_IN | PJM_Rest_of_RTO | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_MI | MISO_IN | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_MI | MISO_WUMS | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_MI | IESO | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_MI | PJM_Rest_of_RTO | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_MO_IL | ENTERGY | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_MO_IL | MISO_IN | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_MO_IL | MISO_W | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_MO_IL | PJM_Rest_of_RTO | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_MO_IL | SPP_N | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_MO_IL | TVA | To obtain the MRM-NEEM Pipe Transfer Limit between TVA and MISO_MO_IL, a linear transfer analysis was performed in PSS(r) MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between TVA and MISO_MO_IL. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies performed in SERC.
MISO_W | MAPP_CA | The pipe values from "MAPP CA" to "MISO W" are documented in operational guide.
MISO_W | MAPP_US | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_W | MISO_MO_IL | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_W | MISO_WUMS | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_W | NE | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_W | IESO | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_W | PJM_Rest_of_RTO | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_W | SPP_N | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
MISO_WUMS | MISO_MI | Historical MISO_WUMS maximum import and export values as well as historical maximum import and export values for the individual "Pipes" connecting to the MISO_WUMS "Bubble" were gathered for the years 2008-2010. The MISO_WUMS maximum import and export values were then augmented by 70% of the rated normal capacity of the new tie facilities or upgraded tie facility ratings. The augmented MISO_WUMS maximum import and export values were then distributed over the "Pipes" connecting to the MISO_WUMS "Bubble" based on the historical maximum import and export values for the individual "Pipes" connecting to the MISO_WUMS "Bubble".
MISO_WUMS | MISO_W | Historical MISO_WUMS maximum import and export values as well as historical maximum import and export values for the individual "Pipes" connecting to the MISO_WUMS "Bubble" were gathered for the years 2008-2010. The MISO_WUMS maximum import and export values were then augmented by 70% of the rated normal capacity of the new tie facilities or upgraded tie facility ratings. The augmented MISO_WUMS maximum import and export values were then distributed over the "Pipes" connecting to the MISO_WUMS "Bubble" based on the historical maximum import and export values for the individual "Pipes" connecting to the MISO_WUMS "Bubble".
MISO_WUMS | PJM_Rest_of_RTO | Historical MISO_WUMS maximum import and export values as well as historical maximum import and export values for the individual "Pipes" connecting to the MISO_WUMS "Bubble" were gathered for the years 2008-2010. The MISO_WUMS maximum import and export values were then augmented by 70% of the rated normal capacity of the new tie facilities or upgraded tie facility ratings. The augmented MISO_WUMS maximum import and export values were then distributed over the "Pipes" connecting to the MISO_WUMS "Bubble" based on the historical maximum import and export values for the individual "Pipes" connecting to the MISO_WUMS "Bubble".
NE | MAPP_US | The values for the pipe from "MAPP US" to "NE" are found using transfer study from generation to generation.
NE | MISO_W | Values were coordinated between SPP and MISO_W and were detemined by averaging the values obtained by the two entities.
NE | RMPA | This is a DC tie to WECC. This value is the current operating limit for the DC tie.
NE | SPP_N | The transfer capacity to SPP_N was determined by using the first valid limiting FCITC transfer value under contingency.
NEISO | NYISO_A-F | The known 1200 MW New York-New England bi directional transfer limit (excluding the PAR controlled 1385 Norwalk-Northport cable at 200 MW and the Cross-Sound HVDC cable at 330 MW) was separated into the regions specified for NYISO in the NEEM bubble diagram. The 398 line (Pleasant Valley-Long Mountain) is the sole line connecting ISO-NE to the “NYISO GHI” region, while the rest of the lines between upstate New York and New England connect to the “NYISO A-F” region. (The 690 line, Salisbury-Smithfield, is open in the EIPC case, as usual, so that is not included in either interface.) Transfers between New York and New England were varied over a range of dispatch assumptions that resulted in an average split of 50/50 of the 1200 MW limit into the A-F and GHI regions resulting in the 600 MW ratings.
NEISO | NYISO_GHI | The known 1200 MW New York-New England transfer limit (excluding the PAR controlled 1385 Norwalk-Northport cable at 200 MW and the Cross-Sound HVDC cable at 330 MW) was separated into the regions specified for NYISO in the NEEM bubble diagram. The 398 line (Pleasant Valley-Long Mountain) is the sole line connecting ISO-NE to the “NYISO GHI” region, while the rest of the lines between upstate New York and New England connect to the “NYISO A-F” region. (The 690 line, Salisbury-Smithfield, is open in the EIPC case, as usual, so that is not included in either interface.) Transfers between New York and New England were varied over a range of dispatch assumptions that resulted in an average split of 50/50 of the 1200 MW limit into the A-F and GHI regions resulting in the 600 MW ratings.
NEISO | NYISO_J_&_K | The known 1200 MW New York-New England bi directional transfer limit (excluding the PAR controlled 1385 Norwalk-Northport cable at 200 MW and the Cross-Sound HVDC cable at 330 MW) was separated into the regions specified for NYISO in the NEEM bubble diagram. The 398 line (Pleasant Valley-Long Mountain) is the sole line connecting ISO-NE to the “NYISO GHI” region, while the rest of the lines between upstate New York and New England connect to the “NYISO A-F” region. (The 690 line, Salisbury-Smithfield, is open in the EIPC case, as usual, so that is not included in either interface.) Transfers between New York and New England were varied over a range of dispatch assumptions that resulted in an average split of 50/50 of the 1200 MW limit into the A-F and GHI regions resulting in the 600 MW ratings.
Non_RTO_Midwest | MISO_IN | Midwest ISO performed First Contingency Incremental Transfer Capability (FCITC) to determine the NEEMs transfer limits. The EIPC 2020 Summer Baseline Infrastructure model was used. The contingency and monitored element files that were used for the EIPC Linear Transfer Analysis (LTA) were used to perform the FCITC calculations. The NEEM regions were used for transfer sources and sinks. Transfers adjusted the load and generation in the transfer source area. Transfers reduced generation in sink area. FCITC analysis was performed using MUST version 8.3.2.
Non_RTO_Midwest | TVA | To obtain the MRM-NEEM Pipe Transfer Limit between TVA and Non_RTO_Midwest, a linear transfer analysis was performed in PSS(r) MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between TVA and Non_RTO_Midwest. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies performed in SERC.
NWPP | MAPP_US | This is a DC tie to WECC. This value is the current operating limit for the DC tie.
NYISO_A-F | NEISO | The known 1200 MW New York-New England bi directional transfer limit (excluding the PAR controlled 1385 Norwalk-Northport cable at 200 MW and the Cross-Sound HVDC cable at 330 MW) was separated into the regions specified for NYISO in the NEEM bubble diagram. The 398 line (Pleasant Valley-Long Mountain) is the sole line connecting ISO-NE to the “NYISO GHI” region, while the rest of the lines between upstate New York and New England connect to the “NYISO A-F” region. (The 690 line, Salisbury-Smithfield, is open in the EIPC case, as usual, so that is not included in either interface.) Transfers between New York and New England were varied over a range of dispatch assumptions that resulted in an average split of 50/50 of the 1200 MW limit into the A-F and GHI regions resulting in the 600 MW ratings.
NYISO_A-F | NYISO_GHI | NYISO performs analysis for the calculation of transfer limits for economic and reliability studies that employ a “pipe and bubble” model.These are done for the NYISO Comprehensive System Planning Process(CSPP) that covered the years 2010 through 2020.The internal pipes transfer limits were taken or derived from the most recent CSPP and represent the total transfer capability of the interface. External ties were coordinated with IESO, NYISO, and PJM. There are any not any differences between the EIPC 2020 roll-up case, the baseline infrastructure case, and the CSPP case that will significantly affect the results of this type of transfer analysis.
NYISO_A-F | IESO | Those numbers are coming from table 5.2 of the Ontario Transmission System document that is published along with the 18-Month Outlook Report. We also performed linear analysis (TLTG – generation to generation transfers) on BI case and the numbers (for some “pipes”) were very close to the ones from table 5.2.
NYISO_A-F | PJM_Rest_of_MAAC | NYISO performs analysis for the calculation of transfer limits for economic and reliability studies that employ a “pipe and bubble” model.These are done for the NYISO Comprehensive System Planning Process(CSPP) that covered the years 2010 through 2020.The internal pipes transfer limits were taken or derived from the most recent CSPP and represent the total transfer capability of the interface. External ties were coordinated with IESO, NYISO, and PJM. There are any not any differences between the EIPC 2020 roll-up case, the baseline infrastructure case, and the CSPP case that will significantly affect the results of this type of transfer analysis.
NYISO_GHI | NEISO | The known 1200 MW New York-New England bi directional transfer limit (excluding the PAR controlled 1385 Norwalk-Northport cable at 200 MW and the Cross-Sound HVDC cable at 330 MW) was separated into the regions specified for NYISO in the NEEM bubble diagram. The 398 line (Pleasant Valley-Long Mountain) is the sole line connecting ISO-NE to the “NYISO GHI” region, while the rest of the lines between upstate New York and New England connect to the “NYISO A-F” region. (The 690 line, Salisbury-Smithfield, is open in the EIPC case, as usual, so that is not included in either interface.) Transfers between New York and New England were varied over a range of dispatch assumptions that resulted in an average split of 50/50 of the 1200 MW limit into the A-F and GHI regions resulting in the 600 MW ratings.
NYISO_GHI | NYISO_A-F | NYISO performs analysis for the calculation of transfer limits for economic and reliability studies that employ a “pipe and bubble” model.These are done for the NYISO Comprehensive System Planning Process(CSPP) that covered the years 2010 through 2020.The internal pipes transfer limits were taken or derived from the most recent CSPP and represent the total transfer capability of the interface. External ties were coordinated with IESO, NYISO, and PJM. There are any not any differences between the EIPC 2020 roll-up case, the baseline infrastructure case, and the CSPP case that will significantly affect the results of this type of transfer analysis.
NYISO_GHI | NYISO_J_&_K | NYISO performs analysis for the calculation of transfer limits for economic and reliability studies that employ a “pipe and bubble” model.These are done for the NYISO Comprehensive System Planning Process(CSPP) that covered the years 2010 through 2020.The internal pipes transfer limits were taken or derived from the most recent CSPP and represent the total transfer capability of the interface. External ties were coordinated with IESO, NYISO, and PJM. There are any not any differences between the EIPC 2020 roll-up case, the baseline infrastructure case, and the CSPP case that will significantly affect the results of this type of transfer analysis. This pipe represents the merging of two pipes from the standard NYISO "pipe" model.
NYISO_GHI | PJM_Eastern_MAAC | NYISO performs analysis for the calculation of transfer limits for economic and reliability studies that employ a “pipe and bubble” model.These are done for the NYISO Comprehensive System Planning Process(CSPP) that covered the years 2010 through 2020.The internal pipes transfer limits were taken or derived from the most recent CSPP and represent the total transfer capability of the interface. External ties were coordinated with IESO, NYISO, and PJM. There are any not any differences between the EIPC 2020 roll-up case, the baseline infrastructure case, and the CSPP case that will significantly affect the results of this type of transfer analysis. This pipe represents the merging of two"bubbles" from the standard NYISO model to account for the RECO load included in the PJM_Eastern_MAAC bubble
NYISO_J_&_K | NEISO | The known 1200 MW New York-New England bi directional transfer limit (excluding the PAR controlled 1385 Norwalk-Northport cable at 200 MW and the Cross-Sound HVDC cable at 330 MW) was separated into the regions specified for NYISO in the NEEM bubble diagram. The 398 line (Pleasant Valley-Long Mountain) is the sole line connecting ISO-NE to the “NYISO GHI” region, while the rest of the lines between upstate New York and New England connect to the “NYISO A-F” region. (The 690 line, Salisbury-Smithfield, is open in the EIPC case, as usual, so that is not included in either interface.) Transfers between New York and New England were varied over a range of dispatch assumptions that resulted in an average split of 50/50 of the 1200 MW limit into the A-F and GHI regions resulting in the 600 MW ratings.
NYISO_J_&_K | NYISO_GHI | NYISO performs analysis for the calculation of transfer limits for economic and reliability studies that employ a “pipe and bubble” model.These are done for the NYISO Comprehensive System Planning Process(CSPP) that covered the years 2010 through 2020.The internal pipes transfer limits were taken or derived from the most recent CSPP and represent the total transfer capability of the interface. External ties were coordinated with IESO, NYISO, and PJM. There are any not any differences between the EIPC 2020 roll-up case, the baseline infrastructure case, and the CSPP case that will significantly affect the results of this type of transfer analysis. This pipe represents the merging of two pipes from the standard NYISO "pipe" model.
IESO | MAPP_CA | For pipe values from "MAPP CA" to "OH" we used an operational guide from IESO.
IESO | MISO_MI | The number is coming from table 5.2 of the Ontario Transmission System document that is published along with the 18-Month Outlook Report. We also performed linear analysis (TLTG – generation to generation transfers) on BI case and the numbers (for some “pipes”) were very close to the ones from table 5.2.
IESO | MISO_W | The number is coming from table 5.2 of the Ontario Transmission System document that is published along with the 18-Month Outlook Report. We also performed linear analysis (TLTG – generation to generation transfers) on BI case and the numbers (for some “pipes”) were very close to the ones from table 5.2.
IESO | NYISO_A-F | Those numbers are coming from table 5.2 of the Ontario Transmission System document that is published along with the 18-Month Outlook Report. We also performed linear analysis (TLTG – generation to generation transfers) on BI case and the numbers (for some “pipes”) were very close to the ones from table 5.2.
PJM_Eastern_MAAC | NYISO_GHI | NYISO performs analysis for the calculation of transfer limits for economic and reliability studies that employ a “pipe and bubble” model.These are done for the NYISO Comprehensive System Planning Process(CSPP) that covered the years 2010 through 2020.The internal pipes transfer limits were taken or derived from the most recent CSPP and represent the total transfer capability of the interface. External ties were coordinated with IESO, NYISO, and PJM. There are any not any differences between the EIPC 2020 roll-up case, the baseline infrastructure case, and the CSPP case that will significantly affect the results of this type of transfer analysis. This pipe represents the merging of two"bubbles" from the standard NYISO model that represent controllable ties and assumptions of the NEEM model.
PJM_Eastern_MAAC | NYISO_J_&_K | NYISO performs analysis for the calculation of transfer limits for economic and reliability studies that employ a “pipe and bubble” model.These are done for the NYISO Comprehensive System Planning Process(CSPP) that covered the years 2010 through 2020.The internal pipes transfer limits were taken or derived from the most recent CSPP and represent the total transfer capability of the interface. External ties were coordinated with IESO, NYISO, and PJM. There are any not any differences between the EIPC 2020 roll-up case, the baseline infrastructure case, and the CSPP case that will significantly affect the results of this type of transfer analysis. This pipe represents the merging of two"bubbles" from the standard NYISO model that represent controllable ties and assumptions of the NEEM model.
PJM_Eastern_MAAC | PJM_Rest_of_MAAC | PJM determined consensus limits with the external interface owners by examining several “data points” and blending methods to reach agreement on the most appropriate initial value for the limits in the MRN-NEEM model. Rollup case interregional linear transfer analysis results, Current OASIS external interface transmission capability data, Actual 2010 hourly interface flow and schedule data for all PJM interfaces, 2010 PJM internal work assessing PJM’s internal interface capability with backbone upgrades
PJM_Rest_of_MAAC | NYISO_A-F | PJM determined consensus limits with the external interface owners by examining several “data points” and blending methods to reach agreement on the most appropriate initial value for the limits in the MRN-NEEM model. Rollup case interregional linear transfer analysis results, Current OASIS external interface transmission capability data, Actual 2010 hourly interface flow and schedule data for all PJM interfaces, 2010 PJM internal work assessing PJM’s internal interface capability with backbone upgrades
PJM_Rest_of_MAAC | PJM_Eastern_MAAC | PJM determined consensus limits with the external interface owners by examining several “data points” and blending methods to reach agreement on the most appropriate initial value for the limits in the MRN-NEEM model. Rollup case interregional linear transfer analysis results, Current OASIS external interface transmission capability data, Actual 2010 hourly interface flow and schedule data for all PJM interfaces, 2010 PJM internal work assessing PJM’s internal interface capability with backbone upgrades
PJM_Rest_of_MAAC | PJM_Rest_of_RTO | PJM determined consensus limits with the external interface owners by examining several “data points” and blending methods to reach agreement on the most appropriate initial value for the limits in the MRN-NEEM model. Rollup case interregional linear transfer analysis results, Current OASIS external interface transmission capability data, Actual 2010 hourly interface flow and schedule data for all PJM interfaces, 2010 PJM internal work assessing PJM’s internal interface capability with backbone upgrades
PJM_Rest_of_RTO | MISO_IN | PJM determined consensus limits with the external interface owners by examining several “data points” and blending methods to reach agreement on the most appropriate initial value for the limits in the MRN-NEEM model. Rollup case interregional linear transfer analysis results, Current OASIS external interface transmission capability data, Actual 2010 hourly interface flow and schedule data for all PJM interfaces, 2010 PJM internal work assessing PJM’s internal interface capability with backbone upgrades and MISO Interface linear transfer analysis using the BI case.
PJM_Rest_of_RTO | MISO_MI | PJM determined consensus limits with the external interface owners by examining several “data points” and blending methods to reach agreement on the most appropriate initial value for the limits in the MRN-NEEM model. Rollup case interregional linear transfer analysis results, Current OASIS external interface transmission capability data, Actual 2010 hourly interface flow and schedule data for all PJM interfaces, 2010 PJM internal work assessing PJM’s internal interface capability with backbone upgrades and MISO Interface linear transfer analysis using the BI case.
PJM_Rest_of_RTO | MISO_MO_IL | PJM determined consensus limits with the external interface owners by examining several “data points” and blending methods to reach agreement on the most appropriate initial value for the limits in the MRN-NEEM model. Rollup case interregional linear transfer analysis results, Current OASIS external interface transmission capability data, Actual 2010 hourly interface flow and schedule data for all PJM interfaces, 2010 PJM internal work assessing PJM’s internal interface capability with backbone upgrades and MISO Interface linear transfer analysis using the BI case.
PJM_Rest_of_RTO | MISO_W | PJM determined consensus limits with the external interface owners by examining several “data points” and blending methods to reach agreement on the most appropriate initial value for the limits in the MRN-NEEM model. Rollup case interregional linear transfer analysis results, Current OASIS external interface transmission capability data, Actual 2010 hourly interface flow and schedule data for all PJM interfaces, 2010 PJM internal work assessing PJM’s internal interface capability with backbone upgrades and MISO Interface linear transfer analysis using the BI case.
PJM_Rest_of_RTO | MISO_WUMS | PJM determined consensus limits with the external interface owners by examining several “data points” and blending methods to reach agreement on the most appropriate initial value for the limits in the MRN-NEEM model. Rollup case interregional linear transfer analysis results, Current OASIS external interface transmission capability data, Actual 2010 hourly interface flow and schedule data for all PJM interfaces, 2010 PJM internal work assessing PJM’s internal interface capability with backbone upgrades and MISO Interface linear transfer analysis using the BI case.
PJM_Rest_of_RTO | PJM_Rest_of_MAAC | PJM determined consensus limits with the external interface owners by examining several “data points” and blending methods to reach agreement on the most appropriate initial value for the limits in the MRN-NEEM model. Rollup case interregional linear transfer analysis results, Current OASIS external interface transmission capability data, Actual 2010 hourly interface flow and schedule data for all PJM interfaces, 2010 PJM internal work assessing PJM’s internal interface capability with backbone upgrades.
PJM_Rest_of_RTO | TVA | To obtain the MRM-NEEM Pipe Transfer Limit between PJM and TVA, OASIS data, operating history, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case, and the existing CRA NEEMS data were reviewed. The data was evaluated and coordinated pipe sizes were determined by PJM and TVA.
PJM_Rest_of_RTO | VACAR | To obtain the MRM-NEEM Pipe Transfer Limit between PJM and VACAR, OASIS data, operating history, and the existing CRA NEEMS data were reviewed; as well as a linear transfer analysis performed with PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The data and analysis results were evaluated and coordinated pipe sizes jointly determined by PJM and VACAR. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning economic and reliability studies.
RMPA | MAPP_US | This is a DC tie to WECC. This value is the current operating limit for the DC tie.
RMPA | NE | This is a DC tie to WECC. This value is the current operating limit for the DC tie.
RMPA | SPP_N | Ties with RMPA were determined as the combined maximum capacity of the DC ties.
SOCO | ENTERGY | To obtain the MRM-NEEM Pipe Transfer Limit between Southern Company and Entergy, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between Southern Company and Entergy. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies performed in SERC.
SOCO | FRCC | The transfer capabilties provided as input in the MRN-NEEM model were obtained from the most recent FRCC - Southern joint TTC study. This interface is a voltage stability limited interface, and therefore, linear analysis on the baseline infrastructure case was not performed. Their are no transmission enhancements that are currently planned that would increase the transfer capability between these regions.
SOCO | TVA | To obtain the MRM-NEEM Pipe Transfer Limit between Southern Company and TVA, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between Southern Company and TVA. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies performed in SERC.
SOCO | VACAR | To obtain the MRM-NEEM Pipe Transfer Limit between Southern Company and VACAR, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between Southern Company and VACAR. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies performed in SERC.
SPP_N | ENTERGY | To obtain the MRN-NEEM Pipe Transfer Limit between SPP and Entergy, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then coordinated between SPP and Entergy.
SPP_N | MISO_MO_IL | The transfer capacity was coordinated between SPP and MISO_MO_IL and were detemined by averaging the values obtained by the two entities.
SPP_N | MISO_W | The transfer capacity was coordinated between SPP and MISO_W and were detemined by averaging the values obtained by the two entities.
SPP_N | NE | The transfer capacity to NE was determined by using the first valid limiting FCITC transfer value under contingency.
SPP_N | RMPA | Ties with RMPA were determined as the combined maximum capacity of the DC ties.
SPP_N | SPP_S | The transfer capacity to SPP_S was determined by using the first valid limiting FCITC transfer value under contingency.
SPP_S | AZ_NM_SNV | Ties with AZ_NM_SW were determined as the combined maximum capacity of the DC ties.
SPP_S | ENTERGY | To obtain the MRN-NEEM Pipe Transfer Limit between SPP and Entergy, a linear transfer analysis was performed in PSS(r) MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then coordinated between SPP and Entergy.
SPP_S | ERCOT | Ties with ERCOT were determined as the combined maximum capacity of the DC ties.
SPP_S | SPP_N | The transfer capacity to SPP_N was determined as the first valid limiting FCITC transfer value under contingency.
TVA | ENTERGY | To obtain the MRM-NEEM Pipe Transfer Limit between TVA and Entergy, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between TVA and Entergy. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies.
TVA | MISO_MO_IL | To obtain the MRM-NEEM Pipe Transfer Limit between TVA and MISO_MO_IL, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between TVA and MISO_MO_IL. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies performed in SERC.
TVA | Non_RTO_Midwest | To obtain the MRM-NEEM Pipe Transfer Limit between TVA and Non_RTO_Midwest, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between TVA and Non_RTO_Midwest. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies performed in SERC.
TVA | PJM_Rest_of_RTO | To obtain the MRM-NEEM Pipe Transfer Limit between PJM and TVA, OASIS data, operating history, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case, and the existing CRA NEEMS data were reviewed. The data was evaluated and coordinated pipe sizes were determined by PJM and TVA.
TVA | SOCO | To obtain the MRM-NEEM Pipe Transfer Limit between Southern Company and TVA, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between Southern Company and TVA. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies performed in SERC.
TVA | VACAR | To obtain the MRM-NEEM Pipe Transfer Limit between TVA and VACAR, the tie line capacity (contract path) between the regions and the results of linear transfer analysis performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case were reviewed. There were no limiting facilities identified at transfer levels below the contract path capacity of the tie lines between the regions. FERC tariff regulations limit the transfer capability to the lower of ATC or contract path capacity.
VACAR | PJM_Rest_of_RTO | To obtain the MRM-NEEM Pipe Transfer Limit between PJM and VACAR, OASIS data, operating history, and the existing CRA NEEMS data were reviewed; as well as a linear transfer analysis performed with PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The data and analysis results were evaluated and coordinated pipe sizes jointly determined by PJM and VACAR. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning economic and reliability studies.
VACAR | SOCO | To obtain the MRM-NEEM Pipe Transfer Limit between Southern Company and VACAR, a linear transfer analysis was performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case. The analysis results were then verified to be valid and coordinated between Southern Company and VACAR. The limiting facilities and associated contingencies identified are consistent with those found in other transmission planning studies performed in SERC.
VACAR | TVA | To obtain the MRM-NEEM Pipe Transfer Limit between TVA and VACAR, the tie line capacity (contract path) between the regions and the results of linear transfer analysis performed in PSS® MUST using the EIPC 2020 Baseline Infrastructure Case were reviewed. There were no limiting facilities identified at transfer levels below the contract path capacity of the tie lines between the regions. FERC tariff regulations limit the transfer capability to the lower of ATC or contract path capacity.